ISBN 978-83-927084-9-0

ISSN 1232-3071

THRESHOLD VELOCITY FOR THE SUSPENSION OF µ-SIZED PARTICLES IN SMOOTH PIPE FLOW

Norbert Eisenhauer1, Bernd Hofmann2, Matthias Maier2, Karl Roth2

1University of Applied Sciences Karlsruhe, Moltkestr. 30, D-76133 Karlsruhe, Germany, Norbert.Eisenhauer@hs-karlsruhe.de

2Stadtwerke Karlsruhe, Dep. of Drinking Water Supply, Municipal Utilities of the City of Karlsruhe, Germany, Bernd.Hofmann@Stadtwerke-Karlsruhe.de, Matthias.Maier@Stadtwerke-Karlsruhe.de, Karl.Roth@Stadtwerke-Karlsruhe.de

Abstract. In drinking water pipes the flow is stagnant, laminar or smooth turbulent with a viscous sublayer for longer periods. Solid µ-sized particles that are embedded in the viscous sublayer of smooth turbulent flow or laminar flow conditions may be moved but there is no turbulence induced lift force that brings the particles into suspension. The suspension of the particles, i.e. the upward move of the particle in a laminar flow, can be explained by the Saffmann-effect and the Magnus-effect. Considering these effects a threshold velocity (in the sense of average flow velocity) for the suspension of µ-sized particles in smooth flow has been set up on the basis of a fully developed logarithmic velocity profile.

KEY WORDS: 	Magnus effect, Saffmann effect, incipient suspension, pipe flow, viscous sublayer

# 1. INTRODUCTION

It is proven that the sedimentation of particles plays an important role for microbiological problems in drinking water distribution systems. The problem is more severe if the pipe diameter was designed for fire-fighting purposes rather than for the domestic water supply of drinking water.

The discharge in drinking water pipes varies in a wide range: from stagnation over laminar flow to fully turbulent flow. Consequently sedimentation cannot be avoided. To remove these particles the system has to be flushed from time to time. Considering the economic aspects the amount of flushing water has to be minimized.  For low flow rates the flow is smooth turbulent with a viscous sublayer. Solid µ-sized particles that are embedded in this sublayer may be moved but there is no turbulence induced lift force that brings the particles into suspension. The suspension of such particles, i.e. the upward move of the particle in a laminar flow can be explained by the Saffmann-effect and the Magnus-effect, Hölzer (2007). On the basis of a fully developed logarithmic velocity profile the threshold velocity (in the sense of average flow velocity) for the suspension of µ-sized particles in smooth turbulent flow is developed. Sediment concentration is so small that no interaction of the particles occurs.

## 2. MAGNUS-EFFECT

Fig.1 shows the flow pattern of a spherical particle that rotates a flow of constant velocity. The flow velocities are higher on the side where the peripheral speed of the particle has the same direction as the surrounding flow. On the opposite side the flow velocities are lower. Consequently there is a pressure difference around the particle that leads to a force in the direction of the higher velocities. This phenomenon has been experimentally investigated and described by Heinrich Gustav Magnus (1802-1870).

Fig. 1 Streamlines around a rotating particle (Magnus-effect), Hölzer (2007)

The Magnus-force FM of a rotating particle is generally given by Hölzer (2007):

(1)

In this equation cM represents the Magnus-coefficient, ρf the fluid density, V the particle volume, u the flow velocity and the rotational speed of the particle.

For laminar flow around a spherical particle with diameter dg the Magnus force is given by Hölzer (2007):

(2)

Assuming that the rotational speed results from the velocity difference ubetween the top and the bottom of the particle

(3)

equations (1) and (2) can be rewritten for a spherical particle as

(4)

(5)

The particle moves upwards when the Magnus force exceeds its submerged weight G’.

(6)

With the equations (4) and (5) the threshold conditions for an upward moving are given by:

(7)

(8)

Table 1 shows the ‘impulse change’ u.u for different grain sizes and densities which is required to move a spherical particle upwards according to equation (8) (laminar flow).

Table 1

Impulse change’ required to move a spherical particle upwards (Magnus effect)

|  | dg [mm] | 0.001 | 0.01 | 0.1 | 1.0 |
| --- | --- | --- | --- | --- | --- |
| u.u[cm²/s²] | g=2500kg/m³ | 0.20 | 1.96 | 19.62 | 196.20 |
| u.u[cm²/s²] | g=5500kg/m³ | 0.59 | 5.89 | 58.86 | 588.60 |

3. SAFFMANN-EFFEKT

When the particle is not rotating a flow induced lift force – the Saffmann force - is generated when there is a velocity gradient over the height of the particle (Fig. 2). Like the Magnus effect the higher flow velocities generate a lower pressure on the top of the particle compared to the bottom.

Fig. 2 Streamlines around a non rotating particle in a flow with velocity gradient, Hölzer (2007)

The Saffmann-force on a spherical particle in a turbulent flow is given by Hölzer (2007)

(9)

where cs is the Saffmann-coefficient. In laminar flow the Saffmann force is calculated as follows, Hölzer (2007):

(10)

Again the particle will be lifted when the Saffmann force exceeds the submerged weight. Similar considerations as in chapter 2 lead to the following threshold conditions for the lift off a spherical particle:

(11)

(12)

Table 2 shows for different grain sizes and densities the slightly modified ‘impulse change’ u.√u that is required to move a spherical particle upwards according to equation (8) (laminar flow).

Table 2

Impulse change’ required to move a spherical particle upwards (Saffmann effect)

|  | dg [mm] | 0.001 | 0.01 | 0.1 | 1.0 |
| --- | --- | --- | --- | --- | --- |
| u.√u[cm/s]3/2 | g=2500kg/m³ | 0.003 | 0.09 | 2.96 | 93.70 |
| u.√u[cm/s]3/2 | g=5500kg/m³ | 0.01 | 0.28 | 8.89 | 281.09 |

## 4. RESULTS OF THE CALCULATION OF THE MEAN THRESHOLD VELOCITY FOR INCIPIENT SUSPENSION

In chapters 2 and 3 it is derived that the lift of a particle depends on impulse change u.u respectively u.√u. For a given velocity distribution it is possible to calculate the impulse change at any point. Hence it is possible to see whether the flow may bring the particle into suspension or not. On the other hand the threshold velocity for suspension can be found. Following assumptions were made:

- Fully developed smooth pipe flow

- In the viscous sublayer (0< y. u* /ν < 5,0) the velocity distribution and its gradient are given by:

(13)

and

(14)

- In the turbulent inner zone (20< y. u* /ν < 105) the velocity distribution and its gradient are given by:

(15)

and

(16)

- The velocity difference of the top and the bottom of a µ-sized (spherical) particle with diameter dg (dg is smaller than the thickness of the viscous sublayer)  is given by:

(viscous sublayer)						(17a)

(inner turbulent zone) 					(17b)

- The friction coefficient  is related to the number of Reynolds and calculated by Zanke’s approach:

(17)

- The shear velocity and the mean velocity of the flow is given by the basic relation:

(18)

In figures 3 and 4 the results of a calculation of the Magnus force and the Saffmann force using equation (18) are exemplarily shown for a particle size of 100 µm. Pipe diameter is 100 mm, the roughness of the pipe was assumed with k=0.1 mm. The impulse changes were calculated for four locations in the flow measured from the wall: 50 µm (d_g/2, half particle size), at the top of the viscous sublayer (delta), at a distance of two sublayers (2delta) and in the center of the pipe (d/2) and different mean flow velocities.

Fig. 3. Impulse change of the Magnus force for four wall distances (dg=100 µm, d= 100mm)

Fig. 4. Impulse change of the Saffmann force for four wall distances (dg=100 µm, d= 100mm)

The figures show that a 100 µm particle (ρs=2500 kg/m³) touching the wall will come into suspension at a flow velocity of approx. 40 cm/s dominated by the Saffmann effect. Repeating the calculation for various pipe and particle diameters, threshold velocities were found according to tables 3 and 4.

Table 4

Threshold velocity resolving the submerged weight of a particle (ρS= 2500 kg/m³)

due to the Saffmann-effect

| Threshold Velocity [m/s] for Incipient Suspension (Saffmann-Effect) | D [m] |
| --- | --- |
|  | 0.1 | 0.3 | 0.8 |
| dg[µm] | 1 | 0.36 | 0.44 | 0.48 |
|  | 10 | 0.36 | 0.43 | 0.47 |
|  | 100 | 0.36 | 0.41 | 0.45 |

Table 5

Threshold velocity resolving the submerged weight of a particle (ρS= 2500 kg/m³)

due to the Magnus-effect

| Threshold Velocity [m/s] for Incipient Suspension (Magnus-Effect) | D [m] |
| --- | --- |
|  | 0.1 | 0.3 | 0.8 |
| dg[µm] | 1 | 1.8 | 2.1 | 2.5 |
|  | 10 | 0.95 | 1.2 | 1.3 |
|  | 100 | 0.5 | 0.6 | 0.65 |

A 100 µm particle (ρs=2500 kg/m³) in a pipe of 100 mm will be suspended at velocities of 0.36 m/s respectively 0.6 m/s. These velocities create a shearstress of 0.43 N/m² resp. 0.77 N/m² and we gain for the dimensionless shear stress τ* (Shields-parameter) values of 0.26 and 0.48. The 100 µm particle is equivalent to a Bonnefille-parameter D* of 2.1. Applying the Shields approach – although Shields did not investigate such small particles – we find according to Zanke, 1982, a threshold value for τ* of 0.69.  The lower value may be explained by the absence of cohesive effects for a lone sphere.

## 5. CONCLUSIONS

From the results presented in the tables above the following conclusions can be drawn:

- Incipient suspension is dominated by the Saffmann effect.

- Pipe and particle diameter have only little influence on the threshold velocity regarding the Saffmann effect.

- The velocity difference between top and bottom of the particle dominates the process as the threshold velocity reduces for larger particle sizes.

REFERENCES

Hölzer, Andreas, 2007. Bestimmung des Widerstandes, Auftriebs und Drehmoments und Simulation der Bewegung nichtsphärischer Partikel in laminaren und turbulenten Strömungen mit dem Lattice-Boltzmann-Verfahren; Dissertation , University of Halle

Zanke, Ulrich, 1982 Grundlagen der Sedimentbewegung, Springer Verlag

# Comments

Würde ich so hreiben, ist vielleicht Geschmackssache.. MM

Stimmt die equation-Nr.? MM

# Text boxes

utop > ubottom

dg

Flow induced lift force FS

dg



u =

Flow induced lift force FM

(Magnus force